## iodam1
~IN |  |  |  |  | to access the definition of the variables in other languages, refer to Engineering dictionary.xls at HERA documentation |  | ~OUT
res_max0_0000_wl | 315 | m | 1 | NAmax | maximum water level of the reservoir | s h | dam_crst_0000_el | 318 | m | 1 | Elcr | dam crest elevation
geo_qual_rock_x | 1 |  | 1 |  | rock quality (1 - good; 2 - medium; 3 - poor) | q h | dam_crst_0000_l | 4 | m | 2 |  | dam crest width
geo_soil_rbed_th | 1 | m | 1 | ete | soil thickness on the riverbed |  | dam_crst_max0_h | 19 | m | 1 |  | maximum dam height
geo_soil_xres_th | 3 | m | 1 | ete | soil thickness on the site of a reservoir | quant | dam_conc_upst_i | 0 |  | 1 | mm | upstream slope of the concrete dam
rtc_dam0_zero_wl | 300 | m | 1 |  | dam rating curve zero | quant | dam_conc_dwst_i | 0.75 |  | 1 | mj | downstream slope of the concrete dam
dam_min0_0000_el | 305 | m | 1 | ? | terrain minimum elevation along the dam axis | div | dam_botm_max0_l | 18.25 | m | 2 |  | dam transversal length
spw_type_0000_x | 4 |  | 2 |  | identification for the spillway type | div | dam_botm_upst_l | 2 | m | 2 |  | dam upstream transversal length
res_type_watc_x | 0 |  |  |  | identification for the reservoir type according to its location (in a watercourse = 0 or not =1) | div | dam_botm_dwst_l | 16.25 | m | 2 |  | dam downstream transversal length
[6 empty] | spw | res_mmax_rise_h | 2 | m | 1 |  | maximum maximorum water level rising
|  |  | 1 |  | IN: project basic information |  | geo_rock_excv_th | 1 | m | 1 |  | rock excavation thickness for concrete structures
[5 empty] | OUT: first results for HERA calculation |  | err_msg0_0000_tx |  |  | 2 |  | error message
|  |  | 2 |  | IN: information obtained by HERA after the first workflow calculation
[5 empty] | OUT: final results obtained after the end of the workflow | [5 empty] | ERROR MESSAGES
[11 empty] | 0 | Error during the dimensioning process. Generate the engineering files of this layout to find it
geo_soil_lbnk_th | 3 | m | 1 | ete | soil thickness on the left riverbank | [5 empty] | 1
geo_soil_rbnk_th | 2 | m | 1 | ete | soil thickness on the right riverbank
novas variáveis na planilha
variáveis não utilizadas, mas que podem vir a ser se passarmos a considerar trechos de barragens
planilhas em que as variáveis são utilizadas

## dam1conc
BARRAGEM DE CONCRETO
DADOS DE ENTRADA
Reservatório em curso d'água | yes
Tipo de vertedouro (1 a 3 = controlado, 4 = livre) | 4
Nível de água máximo normal do reservatório (m) - NAmax | 315
Elevação mínima do terreno ao longo do eixo | 300
Espessura média da camada de solo no trecho de maior altura (m) - ete | 1
Qualidade da rocha de fundação (1 = boa; 2 = média; 3 = ruim) | 1
CARACTERÍSTICAS DA BARRAGEM
Talude do paramento de montante (m) - mm | 0 | padrão = f (geologia - fase 2)
Talude do paramento de jusante (m) - mj | 0.75 | padrão = f (geologia - fase 2)
Largura da crista da barragem (m) | 4 | ver critérios
Altura máxima do nível d'água até a fundação (m) | 16
Borda livre (m) - Hbl | 2 | ver critérios
Sobrelevação máxima para vertedouros livres (m) | 2 | ver critérios
Elevação da crista da barragem (m) | 318 | ver critérios
Altura máxima da barragem (m) | 19
Extensão transversal máxima da barragem (m) | 18.25
Extensão transversal máxima para montante (m) | 2
Extensão transversal máxima para jusante (m) | 16.25
Espessura de sobrescavação em rocha (m) | 1 | f(geologia - fase 2)

## iodam2
~IN |  |  |  |  | to access the definition of the variables in other languages, refer to Engineering dictionary.xls at HERA documentation | ~OUT
res_max0_0000_wl | 315 | m | 1 | NAmax | maximum water level of the reservoir | dam_crst_0000_el | 319 | m | 1 | Elcr | dam crest elevation
res_min0_0000_wl | 310 | m | 1 | NAmin | minimum water level of the reservoir | dam_crst_0000_l | 4 | m | 2 |  | dam crest width
geo_qual_rock_x | 1 |  | 1 |  | rock quality (1 - good; 2 - medium; 3 - poor) | dam_crst_max0_h | 13 | m | 1 |  | maximum dam height
geo_soil_rbed_th | 1 | m | 1 | ete | soil thickness on the riverbed | dam_eart_upst_i | 2.5 |  | 1 | mm | upstream slope of the earthfill dam
geo_soil_xres_th | 2 | m | 1 | ete | soil thickness on the site of a reservoir | dam_eart_dwst_i | 2.2 |  | 1 | mj | downstream slope of the earthfill dam
rtc_dam0_zero_wl | 307 | m | 1 |  | dam rating curve zero | dam_conc_upst_i | 0 |  | 1 | mm | upstream slope of the concrete dam
dam_min0_0000_el | 305 | m | 1 | ? | terrain minimum elevation along the dam axis | dam_conc_dwst_i | 0.75 |  | 1 | mj | downstream slope of the concrete dam
dam_trwl_0001_h | 10 | m | 2 |  | transition wall 1 height (numbering from left to right) | dam_botm_max0_l | 69.1 | m | 2 |  | dam transversal length
dam_trwl_0002_h | 15 | m | 2 |  | transition wall 2 height (numbering from left to right) | dam_botm_upst_l | 36.5 | m | 2 |  | dam upstream transversal length
dam_trwl_0003_h | 35 | m | 2 |  | transition wall 3 height (numbering from left to right) | dam_botm_dwst_l | 32.6 | m | 2 |  | dam downstream transversal length
dam_trwl_0004_h | 25 | m | 2 |  | transition wall 4 height (numbering from left to right) | res_mmax_rise_h | 3 | m | 1 |  | maximum maximorum water level rising
lay_abut_wl01_dt | 200 | m | 2 |  | distance between the transition wall 1 and the left abutment (numbering from left to right) | dam_eart_ripr_el | 309 | m | 1 |  | rip-rap bottom elevation of the earthfill dam
lay_wl02_wl03_dt | 1000 | m | 2 |  | distance between the transition walls 2 and 3 (numbering from left to right) | dam_eart_filt_el | 310 | m | 1 |  | vertical filter top elevation of the earthfill dam
lay_abut_wl04_dt | 400 | m | 2 |  | distance between the transition wall 4 and the right abutment (numbering from left to right) | geo_soil_excv_th | 1 | m | 1 |  | soil excavation thickness for earthfill dams
spw_type_0000_x | 4 |  | 2 |  | identification for the spillway type | geo_rock_excv_th | 1 | m | 1 |  | rock excavation thickness for concrete structures
res_type_watc_x | 0 |  |  |  | identification for the reservoir type according to its location (in a watercourse = 0 or not =1) | lay_abut_wl01_x | 1 | m | 2 |  | layout definition: if zero, there is no wall 1, dam closure in concrete
[6 empty] | lay_wl02_wl03_x | 1 | m | 2 |  | layout definition: if zero, there is no walls, dam closure in concrete
|  |  | 1 |  | IN: project basic information | lay_abut_wl04_x | 1 | m | 2 |  | layout definition: if zero, there is no wall 4, dam closure in concrete
[5 empty] | OUT: first results for HERA calculation | dam_trwl_0001_l | 0 | m | 2 |  | transition wall 1 length (if zero, it´s a retaining wall)
|  |  | 2 |  | IN: information obtained by HERA after the first workflow calculation | dam_trwl_0002_l | 0 | m | 2 |  | transition wall 2 length (if zero, it´s a retaining wall)
[5 empty] | OUT: final results obtained after the end of the workflow | dam_trwl_0003_l | 57.5 | m | 2 |  | transition wall 3 length (if zero, it´s a retaining wall)
[6 empty] | dam_trwl_0004_l | 0 | m | 2 |  | transition wall 4 extension (if zero, it´s a retaining wall)
geo_soil_lbnk_th | 3 | m | 1 | ete | soil thickness on the left riverbank | dam_e0r0_tran_l | 30 | m | 1 |  | transition lenght from the earthfill to the rockfill dam section in case of transition walls
geo_soil_rbnk_th | 2 | m | 1 | ete | soil thickness on the right riverbank | err_msg0_0000_tx |  |  | 2 |  | error message
ERROR MESSAGES
[5 empty] | novas variáveis na planilha |  |  |  |  | 0 | Error during the dimensioning process. Generate the engineering files of this layout to find it
[5 empty] | variáveis não utilizadas, mas que podem vir a ser se passarmos a considerar trechos de barragens |  |  |  |  | 1

## dam2eart
BARRAGEM DE TERRA
DADOS DE ENTRADA |  |  |  | MUROS
Reservatório em curso d'água | yes |  | Quantidade |  | Altura |  | Tipo |  | Extensão
Tipo de vertedouro (1 a 3 = controlado, 4 = livre) | 4 |  | 1 | muro de transição 1 | 10 | m | 1 | muro de encosto | 0 | m
Nível de água máximo normal do reservatório (m) - NAmax | 315 |  | 1 | muro de transição 2 | 15 | m | 1 | muro de encosto | 0 | m
Nível de água mínimo do reservatório (m) - Namin | 310 |  | 1 | muro de transição 3 | 35 | m | 2 | muro de abraço | 57.5 | m
Elevação mínima do terreno ao longo do eixo | 307 |  | 1 | muro de transição 4 | 25 | m | 1 | muro de encosto | 0 | m
Espessura média da camada de solo no trecho de maior altura (m) - ete | 1 |  | 4 | muros de transição
Qualidade da rocha de fundação (1 = boa; 2 = média; 3 = ruim) | 1
CARACTERÍSTICAS DA BARRAGEM
Talude do paramento de montante (m) - mm | 2.5 | padrão = f (geologia - fase 2)
Talude do paramento de jusante (m) - mj | 2.2 | padrão = f (geologia - fase 2)
Largura da crista da barragem (m) | 4 | ver critérios
Altura máxima do nível d'água até a fundação (m) | 9
Borda livre (m) - Hbl | 4 | ver critérios
Sobrelevação máxima para vertedouros livres (m) | 3 | ver critérios
Elevação da crista da barragem (m) | 319 | ver critérios
Altura máxima da barragem (m) | 13
Extensão transversal máxima da barragem (m) | 69.1
Extensão transversal máxima para montante (m) | 36.5
Extensão transversal máxima para jusante (m) | 32.6
Espessura de sobrescavação em solo (m) | 1
Espessura de sobrescavação em rocha (m) | 1 | f(geologia - fase 2)
Elevação inferior do rip-rap (m) | 309
Elevação superior do filtro vertical (m) | 310
Extensão da transição da barragem de terra para enrocamento (m) | 30

## iodam3
~IN |  |  |  |  | to access the definition of the variables in other languages, refer to Engineering dictionary.xls at HERA documentation | ~OUT
res_max0_0000_wl | 236 | m | 1 | NAmax | maximum water level of the reservoir | dam_crst_0000_el | 239 | m | 1 | Elcr | dam crest elevation
geo_qual_rock_x | 1 |  | 1 |  | rock quality (1 - good; 2 - medium; 3 - poor) | dam_crst_0000_l | 4 | m | 2 |  | dam crest width
geo_soil_rbed_th | 1 | m | 1 | ete | soil thickness on the riverbed | dam_crst_max0_h | 20 | m | 1 |  | maximum dam height
geo_soil_xres_th | 1 | m | 1 | ete | soil thickness on the site of a reservoir | dam_rock_upst_i | 1.5 |  | 1 | mm | upstream slope of the rockfill dam
rtc_dam0_zero_wl | 220 | m | 1 |  | dam rating curve zero | dam_rock_dwst_i | 1.5 |  | 1 | mj | downstream slope of the rockfill dam
dam_min0_0000_el | 220 | m | 1 | ? | terrain minimum elevation along the dam axis | dam_conc_upst_i | 0 |  | 1 | mm | upstream slope of the concrete dam
dam_trwl_0001_h | 10 | m | 2 |  | transition wall 1 height (numbering from left to right) | dam_conc_dwst_i | 0.75 |  | 1 | mj | downstream slope of the concrete dam
dam_trwl_0002_h | 15 | m | 2 |  | transition wall 2 height (numbering from left to right) | dam_botm_max0_l | 68 | m | 2 |  | dam transversal length
dam_trwl_0003_h | 20 | m | 2 |  | transition wall 3 height (numbering from left to right) | dam_botm_upst_l | 34 | m | 2 |  | dam upstream transversal length
dam_trwl_0004_h | 10 | m | 2 |  | transition wall 4 height (numbering from left to right) | dam_botm_dwst_l | 34 | m | 2 |  | dam downstream transversal length
lay_abut_wl01_dt | 20 | m | 2 |  | distance between the transition wall 1 and the left abutment (numbering from left to right) | res_mmax_rise_h | 2 | m | 1 |  | maximum maximorum water level rising
lay_wl02_wl03_dt | 150 | m | 2 |  | distance between the transition walls 2 and 3 (numbering from left to right) | geo_rock_excv_th | 1 | m | 1 |  | rock excavation thickness for concrete structures
lay_abut_wl04_dt | 40 | m | 2 |  | distance between the transition wall 4 and the right abutment (numbering from left to right) | lay_abut_wl01_x | 1 | m | 2 |  | layout definition: if zero, there is no wall 1, dam closure in concrete
spw_type_0000_x | 1 |  | 1 |  | identification for the spillway type | lay_wl02_wl03_x | 1 | m | 2 |  | layout definition: if zero, there is no walls, dam closure in concrete
res_type_watc_x | 0 |  |  |  | identification for the reservoir type according to its location (in a watercourse = 0 or not =1) | lay_abut_wl04_x | 1 | m | 2 |  | layout definition: if zero, there is no wall 4, dam closure in concrete
[6 empty] | dam_trwl_0001_l | 0 | m | 2 |  | transition wall 1 length (if zero, it´s a retaining wall)
|  |  | 1 |  | IN: project basic information | dam_trwl_0002_l | 0 | m | 2 |  | transition wall 2 length (if zero, it´s a retaining wall)
[5 empty] | OUT: first results for HERA calculation | dam_trwl_0003_l | 0 | m | 2 |  | transition wall 3 length (if zero, it´s a retaining wall)
|  |  | 2 |  | IN: information obtained by HERA after the first workflow calculation | dam_trwl_0004_l | 0 | m | 2 |  | transition wall 4 extension (if zero, it´s a retaining wall)
[5 empty] | OUT: final results obtained after the end of the workflow | err_msg0_0000_tx |  |  | 2 |  | error message
geo_soil_lbnk_th | 3 | m | 1 | ete | soil thickness on the left riverbank |  |  |  |  | ERROR MESSAGES
geo_soil_rbnk_th | 2 | m | 1 | ete | soil thickness on the right riverbank |  |  |  |  | 0 | Error during the dimensioning process. Generate the engineering files of this layout to find it
1
novas variáveis na planilha
variáveis não utilizadas, mas que podem vir a ser se passarmos a considerar trechos de barragens

## dam3rock
BARRAGEM DE TERRA
DADOS DE ENTRADA |  |  |  | MUROS
Reservatório em curso d'água | yes |  | Quantidade |  | Altura |  | Tipo |  | Extensão
Tipo de vertedouro (1 a 3 = controlado, 4 = livre) | 1 |  | 1 | muro de transição 1 | 10 | m | 1 | muro de encosto | 0 | m
Nível de água máximo normal do reservatório (m) - NAmax | 236 |  | 1 | muro de transição 2 | 15 | m | 1 | muro de encosto | 0 | m
Elevação mínima do terreno ao longo do eixo | 220 |  | 1 | muro de transição 3 | 20 | m | 1 | muro de encosto | 0 | m
Espessura média da camada de solo no trecho de maior altura (m) - ete | 1 |  | 1 | muro de transição 4 | 10 | m | 1 | muro de encosto | 0 | m
Qualidade da rocha de fundação (1 = boa; 2 = média; 3 = ruim) | 1 |  | 4 | muros de transição
CARACTERÍSTICAS DA BARRAGEM
Talude do paramento de montante (m) - mm | 1.5 | padrão = f (geologia - fase 2)
Talude do paramento de jusante (m) - mj | 1.5 | padrão = f (geologia - fase 2)
Largura da crista da barragem (m) | 4 | ver critérios
Altura máxima do nível d'água até a fundação (m) | 17
Borda livre (m) - Hbl | 3 | ver critérios
Sobrelevação máxima para vertedouros livres (m) | 2 | ver critérios
Elevação da crista da barragem (m) | 239 | ver critérios
Altura máxima da barragem (m) | 20
Extensão transversal máxima da barragem (m) | 68
Extensão transversal máxima para montante (m) | 34
Extensão transversal máxima para jusante (m) | 34
Espessura de sobrescavação em rocha (m) | 1 | f(geologia - fase 2)

## iodyk1
~IN |  |  |  |  | to access the definition of the variables in other languages, refer to Engineering dictionary.xls at HERA documentation | ~OUT
res_max0_0000_wl | 315 | m | 1 | NAmax | maximum water level of the reservoir | dyk_crst_0000_el | 316 | m | 1 |  | dyke crest elevation
res_min0_0000_wl | 310 | m | 1 | NAmin | minimum water level of the reservoir | dyk_crst_0000_l | 4 | m | 2 |  | dyke crest width
geo_qual_rock_x | 1 |  | 1 |  | rock quality (1 - good; 2 - medium; 3 - poor) | dyk_crst_max0_h | 316 | m | 1 |  | maximum dyke height
geo_soil_xres_th | 1 | m | 1 | ete | soil thickness on the site of a reservoir | dyk_conc_upst_i | 0 |  | 1 |  | upstream slope of the earthfill dyke
dyk_min0_0000_el | 308 | m | 1 |  | terrain minimum elevation along the dyke axis | dyk_conc_dwst_i | 0.75 |  | 1 |  | downstream slope of the earthfill dyke
res_type_watc_x | 1 |  | 2 |  | identification for the reservoir type according to its location (in a watercourse = 0 or not =1) | dyk_botm_max0_l | 10.75 | m | 2 |  | dyke transversal length
[6 empty] | dyk_botm_upst_l | 8.75 | m | 2 |  | dyke upstream transversal length
|  |  | 1 |  | IN: project basic information | dyk_botm_dwst_l | 2 | m | 2 |  | dyke downstream transversal length
[5 empty] | OUT: first results for HERA calculation | geo_soil_excv_th | 1 | m | 1 |  | soil excavation thickness for earthfill dams
|  |  | 2 |  | IN: information obtained by HERA after the first workflow calculation | err_msg0_0000_tx |  |  | 2 |  | error message
OUT: final results obtained after the end of the workflow
ERROR MESSAGES
[10 empty] | 0 | Error during the dimensioning process. Generate the engineering files of this layout to find it
[5 empty] | novas variáveis na planilha |  |  |  |  | 1
variáveis cuja utilidade deve ser verificada

## dyk1conc
DIQUE DE TERRA
DADOS DE ENTRADA
Reservatório em curso d'água | no
Nível de água máximo normal do reservatório (m) - NAmax | 315
Nível de água mínimo do reservatório (m) - Namin | 310
Elevação mínima do terreno ao longo do eixo | 308
Espessura média da camada de solo no trecho de maior altura (m) - ete | 1
Qualidade da rocha de fundação (1 = boa; 2 = média; 3 = ruim) | 1
CARACTERÍSTICAS DA BARRAGEM
Talude do paramento de montante (m) - mm | 0 | padrão = f (geologia - fase 2)
Talude do paramento de jusante (m) - mj | 0.75 | padrão = f (geologia - fase 2)
Largura da crista do dique (m) | 4 | ver critérios
Altura máxima do nível d'água até a fundação (m) | 8
Borda livre (m) - Hbl | 1 | ver critérios
Elevação da crista do dique (m) | 316 | ver critérios
Altura máxima do dique (m) | 9
Extensão transversal máxima do dique (m) | 10.75
Extensão transversal máxima para montante (m) | 8.75
Extensão transversal máxima para jusante (m) | 2
Espessura de sobrescavação em rocha (m) | 1 | f(geologia - fase 2)

## iodyk2
~IN |  |  |  |  | to access the definition of the variables in other languages, refer to Engineering dictionary.xls at HERA documentation | ~OUT
res_max0_0000_wl | 315 | m | 1 | NAmax | maximum water level of the reservoir | dyk_crst_0000_el | 317 | m | 1 |  | dyke crest elevation
res_min0_0000_wl | 310 | m | 1 | NAmin | minimum water level of the reservoir | dyk_crst_0000_l | 4 | m | 2 |  | dyke crest width
geo_qual_rock_x | 1 |  | 1 |  | rock quality (1 - good; 2 - medium; 3 - poor) | dyk_crst_max0_h | 317 | m | 1 |  | maximum dyke height
geo_soil_xres_th | 1 | m | 1 | ete | soil thickness on the site of a reservoir | dyk_eart_upst_i | 2.5 |  | 1 |  | upstream slope of the earthfill dyke
dyk_min0_0000_el | 308 | m | 1 |  | terrain minimum elevation along the dyke axis | dyk_eart_dwst_i | 2.2 |  | 1 |  | downstream slope of the earthfill dyke
res_type_watc_x | 1 |  | 2 |  | identification for the reservoir type according to its location (in a watercourse = 0 or not =1) | dyk_botm_max0_l | 51 | m | 2 |  | dyke transversal length
[6 empty] | dyk_botm_upst_l | 24 | m | 2 |  | dyke upstream transversal length
|  |  | 1 |  | IN: project basic information | dyk_botm_dwst_l | 27 | m | 2 |  | dyke downstream transversal length
[5 empty] | OUT: first results for HERA calculation | dyk_eart_ripr_el | 309 | m | 1 |  | rip-rap bottom elevation of the earthfill dyke
|  |  | 2 |  | IN: information obtained by HERA after the first workflow calculation | dyk_eart_filt_el | 310 | m | 1 |  | vertical filter top elevation of the earthfill dyke
[5 empty] | OUT: final results obtained after the end of the workflow | geo_soil_excv_th | 1 | m | 1 |  | soil excavation thickness for earthfill dams
[6 empty] | err_msg0_0000_tx |  |  | 2 |  | error message
[5 empty] | novas variáveis na planilha |  |  |  |  | ERROR MESSAGES
[5 empty] | variáveis cuja utilidade deve ser verificada |  |  |  |  | 0 | Error during the dimensioning process. Generate the engineering files of this layout to find it
1

## dyk2eart
DIQUE DE TERRA
DADOS DE ENTRADA
Reservatório em curso d'água | no
Nível de água máximo normal do reservatório (m) - NAmax | 315
Nível de água mínimo do reservatório (m) - Namin | 310
Elevação mínima do terreno ao longo do eixo | 308
Espessura média da camada de solo no trecho de maior altura (m) - ete | 1
Qualidade da rocha de fundação (1 = boa; 2 = média; 3 = ruim) | 1
CARACTERÍSTICAS DA BARRAGEM
Talude do paramento de montante (m) - mm | 2.5 | padrão = f (geologia - fase 2)
Talude do paramento de jusante (m) - mj | 2.2 | padrão = f (geologia - fase 2)
Largura da crista do dique (m) | 4 | ver critérios
Altura máxima do nível d'água até a fundação (m) | 8
Borda livre (m) - Hbl | 2 | ver critérios
Elevação da crista do dique (m) | 317 | ver critérios
Altura máxima do dique (m) | 10
Extensão transversal máxima do dique (m) | 51
Extensão transversal máxima para montante (m) | 24
Extensão transversal máxima para jusante (m) | 27
Espessura de sobrescavação em rocha (m) | 1 | f(geologia - fase 2)
Elevação inferior do rip-rap (m) | 309
Elevação superior do filtro vertical (m) | 310

## iodyk3
~IN |  |  |  |  | to access the definition of the variables in other languages, refer to Engineering dictionary.xls at HERA documentation | ~OUT
res_max0_0000_wl | 315 | m | 1 | NAmax | maximum water level of the reservoir | dyk_crst_0000_el | 317 | m | 1 |  | dyke crest elevation
res_min0_0000_wl | 310 | m | 1 | NAmin | minimum water level of the reservoir | dyk_crst_0000_l | 4 | m | 2 |  | dyke crest width
geo_qual_rock_x | 1 |  | 1 |  | rock quality (1 - good; 2 - medium; 3 - poor) | dyk_crst_max0_h | 317 | m | 1 |  | maximum dyke height
geo_soil_xres_th | 1 | m | 1 | ete | soil thickness on the site of a reservoir | dyk_rock_upst_i | 1.5 |  | 1 |  | upstream slope of the earthfill dyke
dyk_min0_0000_el | 308 | m | 1 |  | terrain minimum elevation along the dyke axis | dyk_rock_dwst_i | 1.5 |  | 1 |  | downstream slope of the earthfill dyke
res_type_watc_x | 1 |  | 2 |  | identification for the reservoir type according to its location (in a watercourse = 0 or not =1) | dyk_botm_max0_l | 34 | m | 2 |  | dyke transversal length
[6 empty] | dyk_botm_upst_l | 17 | m | 2 |  | dyke upstream transversal length
|  |  | 1 |  | IN: project basic information | dyk_botm_dwst_l | 17 | m | 2 |  | dyke downstream transversal length
[5 empty] | OUT: first results for HERA calculation | geo_soil_excv_th | 1 | m | 1 |  | soil excavation thickness for earthfill dams
|  |  | 2 |  | IN: information obtained by HERA after the first workflow calculation | err_msg0_0000_tx |  |  | 2 |  | error message
OUT: final results obtained after the end of the workflow
ERROR MESSAGES
[10 empty] | 0 | Error during the dimensioning process. Generate the engineering files of this layout to find it
[5 empty] | novas variáveis na planilha |  |  |  |  | 1
variáveis cuja utilidade deve ser verificada

## dyk3rock
DIQUE DE TERRA
DADOS DE ENTRADA
Reservatório em curso d'água | no
Nível de água máximo normal do reservatório (m) - NAmax | 315
Nível de água mínimo do reservatório (m) - Namin | 310
Elevação mínima do terreno ao longo do eixo | 308
Espessura média da camada de solo no trecho de maior altura (m) - ete | 1
Qualidade da rocha de fundação (1 = boa; 2 = média; 3 = ruim) | 1
CARACTERÍSTICAS DA BARRAGEM
Talude do paramento de montante (m) - mm | 1.5 | padrão = f (geologia - fase 2)
Talude do paramento de jusante (m) - mj | 1.5 | padrão = f (geologia - fase 2)
Largura da crista do dique (m) | 4 | ver critérios
Altura máxima do nível d'água até a fundação (m) | 8
Borda livre (m) - Hbl | 2 | ver critérios
Elevação da crista do dique (m) | 317 | ver critérios
Altura máxima do dique (m) | 10
Extensão transversal máxima do dique (m) | 34
Extensão transversal máxima para montante (m) | 17
Extensão transversal máxima para jusante (m) | 17
Espessura de sobrescavação em rocha (m) | 1 | f(geologia - fase 2)